## Heat Mode
Test # | Test | Zen V1 | Mysa LV | General Notes/Bugs | Build | Pass/Fail
Heat Mode Setpoint Below Ambient
H-001 | Drop setpoint to minimal: | No lights come on unless G is already on | No lights come on unless G is already on |  | Mar 11th | Pass
| - Wait 6-7 minutes | No lights come on, If G is on it shuts off | No lights come on |  | Mar 11th | Pass
| - Wait 10 minutes | No lights come on | No lights come on |  | Mar 11th | Pass
H-002 | Move setpoint 4-5 degrees below ambient: | No lights come on | No lights come on |  | Mar 11th | Pass
| - Wait 5 minutes | No lights come on | No lights come on |  | Mar 11th | Pass
| - Reboot | No lights come on | No lights come on |  | Mar 11th | Pass
H-003 | Push setpoint 2-3 over ambient, allow lights to come on then move back to 1 degrees below: | W1 and G come on, W1 shuts off when changed back | W1 and G come on, W1 and G shut off |  | Mar 11th | Pass
| - Wait 5-6 minutes | G shuts off | All lights off |  | Mar 11th | Pass
Heat Mode Setpoint Above Ambient - Refresh CONFIG
H-004 | Setpoint = ambient | No lights come on | No lights come on |  | Mar 11th | Pass
H-005 | Setpoint 3 degrees above ambient: | W1 and G come on within 1 minute | W1 and G come on within 1 minute | Our G comes on right away, small delay on Zen | Mar 11th | Pass
| - Within 10 minutes | W2 comes on with W1 and G | W2 comes on with W1 and G |  | Mar 11th | Pass
H-006 | Go below ambient, then set setpoint to max temp: | W1 comes on, G stayed on | W1 comes on, G comes on |  | Mar 11th | Pass
| - Reboot at setpoint max temp | W1, W2, G come on | W1, W2 G come on |  | Mar 11th | Pass
H-007 | Drop back to 1 degree above ambient | W1, W2 stays on, G stays on | W1, W2 stays on, G stays on |  | Mar 11th | Pass
H-008 | Drop back setpoint below ambient: | W1, W2 shut off | W1, W2, G shut off |  | Mar 11th | Pass
| - After 2-3 minutes | G shuts off | All Lights stay off |  | Mar 11th | Pass
| - Reboot | All lights stay off | All lights stay off |  | Mar 11th | Pass
OFF Mode w Heat - Refresh CONFIG
Setpoint is above the ambient
H-009 | Change the mode to OFF: | W1, W2 shut off if on | W1, W2, G shut off if on | B-005 Device does not show ambient when off | Mar 11th | Pass
| - After 3+ minutes | G shuts off if on | All lights stay off |  | Mar 11th | Pass
| - Reboot | The device stays off | The device stays off |  | Mar 11th | Pass
H-010 | Try and alter the setpoint | Changes cannot be made when device is off | Changes cannot be made when device is off |  | Mar 11th | Pass
H-011 | Turn back on Heat mode: | W1, W2 and G come on | W1, W2 and G come on |  | Mar 11th | Pass
| Setpoint is below the ambient | G stays on | G stays on
H-012 | Change the mode to OFF: | G stays on(if on) | G shuts off if on | B-005 Device does not show ambient when off | Mar 4th | Pass
| - After 3+ minutes | G turns off | G stays off |  | Mar 4th | Pass
H-013 | Turn back on Heat mode | No lights come on | No lights come on |  | Mar 4th | Pass
Heat Mode to Fan Mode - Refresh CONFIG
H-014 | Switch from Heat mode with W1, W2 on to Fan mode: | N/A | W1, W2 shut off, G stays on |  | Mar 4th | Pass
| - After 5+ minutes | N/A | G stays on |  | Mar 4th | Pass
| - Reboot and wait 12+ minutes | N/A | G stays on |  | Mar 4th | Pass
H-015 | Switch from Fan mode back to Heat mode: | N/A | Nothing comes on |  | Mar 4th | Pass
| - After 12 minutes | N/A | W1,W2,G come on |  | Mar 4th | Pass
H-016 | Reduce heat below ambient(lights off) and switch to Fan mode: | N/A | G stays on |  | Mar 4th | Pass
| - Reboot | N/A | G stays on |  | Mar 4th | Pass
H-017 | Switch from Fan mode to OFF: | N/A | G shuts off | B-005 Device does not show ambient when off | Mar 4th | Pass
| - After 3 minutes | N/A | G stays off |  | Mar 4th | Pass
H-018 | Switch from OFF to Fan mode. | N/A | G comes on |  | Mar 4th | Pass
Fan Speed Test not avaliable
Heat Mode to Auto Mode

## Cool Mode
Test # | Test | Zen V1 | Mysa LV | General Notes/Bugs | Build | Pass/Fail
| C Mode Setpoint Above Ambient |  |  |  | 2.0/Feb 4th
C-001 | Switch from Heat W1, W2 and G on to Cool: | Only G stays on | G shuts off |  | Mar 5th | Pass
| - Wait 3 minutes+ | G shuts off | G stays off |  | Mar 5th | Pass
C-002 | Drop setpoint to 1 degrees above ambient: | All lights stay off | All lights stay off |  | Mar 5th | Pass
| - Wait 5 minutes+ | All lights stay off | All lights stay off |  | Mar 5th | Pass
C-003 | Push setpoint to max: | All lights stay off | All lights stay off |  | Mar 5th | Pass
| - Wait 10+ minutes | All lights stay off | All lights stay off |  | Mar 5th | Pass
| - Reboot | All lights stay off | All lights stay off |  | Mar 5th | Pass
C-004 | Push setpoint under ambient, allow lights to come on then move back to 3 degrees above: | All lights shut off | All lights shut off |  | Mar 5th | Pass
| - Wait 3 minutes+ | All lights stay off | All lights stay off |  | Mar 5th | Pass
C Mode Setpoint Below Ambient - Refresh CONFIG
C-005 | Setpoint = ambient | All lights stay off | All lights stay off |  | Mar 5th | Pass
C-006 | Setpoint 2 below ambient: | Nothing comes on | Nothing comes on |  | Mar 5th | Pass
| - After 3-5 minutes | Y1, G come on | Y1, G come on |  | Mar 5th | Pass
| - After 12 minutes | Y2 comes on | Y2 comes on |  | Mar 5th | Pass
C-007 | Go above ambient, then set setpoint to lowest temp: | Nothing comes on | Nothing comes on |  | Mar 5th | Pass
| - After 17-20 minutes | Y1, Y2, and G comes on | Y1, Y2, and G comes on | Can someone explain this long delay to me? | Mar 5th | Pass
| - Reboot | Nothing comes on | Nothing comes on |  | Mar 5th | Pass
| - After 5 minutes | Y1, Y2 and G come on | Y1, Y2 and G come on |  | Mar 5th | Pass
C-008 | Drop back to 1 degree below ambient: | Y1, Y2 and G stay on | Y1, Y2 and G stay on |  | Mar 5th | Pass
| - After 10 minutes | Y1, Y2 and G stay on | Y1, Y2 and G stay on |  | Mar 5th | Pass
C-009 | Move setpoint above ambient: | All lights shut off | All lights shut off |  | Mar 5th | Pass
| - Reboot | All lights stay off | All lights stay off |  | Mar 5th | Pass
C-010 | Switch to Heat mode: | W1, G come on, W2 if setpoint is high | W1, G come on, W2 if setpoint is high | W2 didnt come on with 5 spread? | Mar 5th | Pass
| - Move setpoint below ambient | W1, W2 Shut off, G stays on | W1, W2 and G shutoff |  | Mar 5th | Pass
| - Switch back to cool | W1, and W2 stay off, G stays on | All stay off |  | Mar 5th | Pass
| - After 5 minutes | Y1, Y2 and G come on | Y1, Y2 and G come on |  | Mar 5th | Pass
| - Push setpoint above ambient | All lights shut off | All lights shut off |  | Mar 5th | Pass
OFF Mode w Cool: All Settings - Refresh CONFIG
Setpoint is below the ambient:
C-011 | Change the mode to OFF | Y1, Y2 and G shut off | Y1, Y2 and G shut off | B-005 Device does not show ambient when off | Mar 5th | Pass
C-012 | Try and alter the setpoint: | Changes cannot be made when device is off | Changes cannot be made when device is off | B-023 - Noise played when setpoint pushed | Mar 4th | Fail
| - Reboot | The device stays off | The device stays off |  | Mar 5th | Pass
C-013 | Turn back on Cool mode: | No lights come on | No lights come on |  | Mar 5th | Pass
| - After 3+ minutes | Y1, Y2 and G come on | Y1, Y2 and G come on |  | Mar 5th | Pass
| Setpoint is above the ambient: | G stays on | G stays on
C-014 | Change the mode to OFF | All lights stay off | All lights stay off | B-005 Device does not show ambient when off | Mar 5th | Pass
C-015 | Turn back on Cool mode | No lights come on | No lights come on |  | Mar 5th | Pass
C Mode to Fan Mode - Refresh CONFIG
C-016 | Switch from Cool mode with Y1, Y2 on to Fan mode: | N/A | Y1, Y2 shut off, G stays on |  | Mar 5th | Pass
| - After 5 minutes | N/A | G stays on |  | Mar 5th | Pass
| - Reboot and wait 12+ minutes | N/A | G stays on |  | Mar 5th | Pass
C-017 | Switch from Fan mode to Cool mode with lights on: | N/A | G shuts off |  | Mar 5th | Pass
| - After 18 minutes | N/A | Y1, Y2 and G come on |  | Mar 5th | Pass
C-018 | Increase setpoint above ambient and switch to Fan mode: | N/A | G comes on |  | Mar 5th | Pass
| - Reboot | N/A | G stays on |  | Mar 5th | Pass
C-019 | Switch from Fan mode to OFF: | N/A | G shuts off | B-005 Device does not show ambient when off | Mar 5th | Pass
| - After 3 minutes | N/A | G stays off |  | Mar 5th | Pass
C-020 | Switch from OFF to Fan mode. | N/A | G turns on |  | Mar 5th | Pass
C-021 | Switch from Cool mode with Y1 to Fan mode: | N/A | Y1 shuts off, G stays on, setpoint cannot be altered |  | Mar 5th
| - After 5+ minutes | N/A | G stays on |  | Mar 5th
Fan Speed Test not avaliable
Cool Mode to Auto Mode

## PairingConfig
Test # | Test | Zen V1 | Mysa LV | Notes | Build
Configuration/Pairing
CP-001 | Select Bluetooth Icon | Different process | Configuration screen is loaded and works as expected |  | Mar 11th
| Select the CONF code | Different process | After the CONF code is selected, the PREF window is loaded. |  | 11th
| Select a mix of PREF and push down | Different process | The proper PREF are set for the code, ambient temp is displayed, off mode is default |  | Mar 4th
CP-002 | Reboot Device | Ambient is displayed | Ambient is displayted |  | Mar 4th
| - Wait 5+ minutes | All lights come on as expected | All lights come on as expected |  | Mar 4th

## GeneralMisc
Test # | Test | Zen V1 | Mysa LV | General Notes/Bugs | Build
General Changes Noted:
G-001 | Temperature Issues: | Device is typically 2 degrees lower ambient | Device typically reads 2 degrees higher ambient | Temp Calibration Issues | Mar 11th
|  | Max is 37, Min is 4 | Max is 30, Min is 5 |  | Mar 11th
| Options Changes: | Many options have been removed | Fade, Light, etc |  | Mar 11th
|  | Menu layout has changed Modes would be scrolled through using left and right | Now we select mode and use up and down |  | Mar 11th
|  | Configuration done manually with button | Configuration done on the device |  | Mar 11th
| GUI/Display: | Removal of physical config buttons | Done on the device |  | Mar 11th
|  | Caution button visible | No |  | Mar 11th
|  | Wifi button visible | No |  | Mar 11th
|  | Mode icons visible | Yes |  | Mar 11th
|  | Phase icons visible | No |  | Mar 11th
|  | Waterfall changes when scrolling setpoint | Basic changes when scrolling setpoint |  | Mar 11th
|  | Fan Mode visible and can change with it | Fan behaviour has changed as documented |  | Mar 11th
|  | After rebooting, shows the ambient temp | After rebooting, shows the ambient temp |  | Mar 11th
Misc Options/Settings
G-002 | Switch between English and French, explore all areas/modes | All headings and areas of the firmware are in French | All headings and areas of the firmware are in French | LV-08, LV-10 sometimes noted | Mar 11th
| - Turn off device, after exploring, turn back on | All headings and areas of the firmware are in French | All headings and areas of the firmware are in French |  | Mar 11th
G-003 | Switch between French and English, explore all areas/modes | All headings and areas of the firmware are in English | All headings and areas of the firmware are in English | LV-08, LV-10 sometimes noted | Mar 11th
| - Turn off device, after exploring, turn back on | All headings and areas of the firmware are in English | All headings and areas of the firmware are in English |  | Mar 11th
G-004 | Switch to C to F in Heat mode | Ambient and setpoint are displayed in F | Ambient and setpoint are displayed in F | LV-08, LV-10 sometimes noted | Mar 11th
| - Test the setpoint above ambient with Heat and Cool | Heat and Cool displayed in F | Heat and Cool displayed in F |  | Mar 11th
| - After 10 minutes | Heat and Cool displayed in F | Heat and Cool displayed in F |  | Mar 11th
| - Turn off device | Heat and Cool displayed in F | Heat and Cool displayed in F |  | Mar 11th
| - Test the setpoint below ambient with Heat and Cool | Heat and Cool displayed in F | Heat and Cool displayed in F |  | Mar 11th
G-005 | Test F with OFF, Fan, and EMERG modes | OFF, Fan, EMERG still use F | OFF, Fan, EMERG still use F |  | Mar 11th
G-006 | Switch from F to C in Cool mode: | Heat and Cool displayed in C | Heat and Cool displayed in C | LV-08, LV-10 sometimes noted | Mar 11th
| - Test the setpoint above ambient with Heat and Cool | Heat and Cool displayed in C | Heat and Cool displayed in C |  | Mar 11th
| - After 10 minutes | Heat and Cool displayed in C | Heat and Cool displayed in C |  | Mar 11th
| - Turn off device | Heat and Cool displayed in C | Heat and Cool displayed in C |  | Mar 11th
| - Test the setpoint below ambient with Heat and Cool | Heat and Cool displayed in C | Heat and Cool displayed in C |  | Mar 11th

## Specific Config Testing
Test Condition | Starting Conditions ("Pre-conditions") |  |  |  | Trigger | Expected Result | Notes | Build | Pass/Fail
Config/System Type/Description | Mode | Ambient | Setpoint | Lights
06B - Forced Air Cooling No Heat, 2 Stage Cool, With Fan | [8 empty] | Pass
Cooling doesn't engage until required | Cool | 20 | 24 | All Off | Lower setpoint to 20. | No lights come on
- Reboot | Cool | 20 | 20 | All off | Reboot the device and wait 10 minutes | No lights come on
Cooling phase 1 engages once required | Cool | 20 | 24 | All Off | Lower setpoint to 19. | Y1, G1 turn on. After 10 minutes, Y2 comes on
Cooling stops if setpoint is dropped below ambient | Cool | 20 | 19 | Y1, Y2, G | Raise setpoint to 20. | Y1, Y2, G turn off
Cooling doesn't engage if ambient is raised | Cool | 20 | 20 | All Off | Raise ambient to 24 | No lights come on
Cooling engages if ambient raised above setpoint | Cool | 24 | 24 | All Off | Raise ambient to 25 | Y1, G1 turn on
Cooling phase 2 engages once required | Cool | 25 | 24 | Y1, G | Raise ambient to 30 | Y1, G1 stay on, Y2 comes on
Status maintained through Reboot | Cool | 30 | 24 | Y1, Y2, G | Reboot the device | Nothing on initially, after 10 minutes Y1, Y2 and G come on
OFF status works as intended | Cool/OFF | 30 | 24 | Y1, Y2, G | Set the mode to OFF | All lights go off, turn back on and lights should come back
Cooling stops when ambient reaches setpoint. | Cool | 30 | 24 | Y1, Y2, G | Lower ambient to 24. | All lights go off
Cooling to Fan mode - Lights off | Cool/Fan | 24 | 24 | All Off | - Change to Fan mode. - Try and move setpoint - Wait 5+ minutes | - G comes on and stays on - Setpoint cannot be changed
Fan mode back to cooling | Fan/Cool | 24 | 24 | G | - Change to Cool Mode - Move setpoint below ambient.(22) | - All lights shut off - Y1 and G comes back on.
Cooling to Fan mode - Lights on | Cool/Fan | 24 | 22 | Y1, G | - Change to Fan mode. - Try and move setpoint - Wait 5+ minutes | - All lights shut off except G - Setpoint cannot be changed.
Pass
60D - Forced Air Heating with Oil/Gas 2 Stage Heat, No Cool, With Fan, With EMERG | [7 empty] | 4.0/Feb 11th | Pass
Heating doesn't engage until required | Heat | 20 | 18 | All Off | Lower setpoint to 16 | No lights come on
- Reboot | Heat | 20 | 16 | All Off | Reboot the device and wait 10 minutes | No lights come on
Heating phase 1 engages once required | Heat | 20 | 16 | All Off | Raise setpoint to 23. | W1, G turn on, after 10 minutes W2 comes on
Heating stops if ambient is raised to equal setpoint | Heat | 20 | 23 | W1, W2, G | Raise ambient to 23 | W1, W2 shut off, G shuts off 3 minutes later
Heating phase 2 engage if ambient is lowered below setpoint | Heat | 23 | 23 | All Off | Lower ambient to 17 | W1, W2, G turn on
Heating stays on if ambient is raised but still below setpoint | Heat | 17 | 23 | W1, W2, G | Raise Ambient to 22 | All lights stay on
Status maintained through Reboot | Heat | 22 | 23 | W1, W2, G | Reboot the device | Nothing on initially, after 10 minutes W1, W2 and G come on
OFF status works as intended | Heat/OFF | 22 | 23 | W1, W2, G | Set the mode to OFF | All lights go off, turn back on and lights should come back
Heating stops when ambient reaches setpoint. | Heat | 22 | 23 | W1, G | Raise ambient to 24 | All lights go off
Heating to Fan mode - Lights off | Heat/Fan | 24 | 24 | All Off | - Change to Fan mode. - Try and move setpoint - Wait 5+ minutes | - G comes on and stays on - Setpoint cannot be changed
Fan mode back to Heat | Fan/Heat | 24 | 24 | G | - Change to Cool Mode - Move setpoint above ambient.(25) | - All lights shut off - W1 and G comes back on.
Heating to Fan mode - Lights on | Heat/Fan | 24 | 22 | W1, G | - Change to Fan mode. - Try and move setpoint - Wait 5+ minutes | - All lights shut off except G - Setpoint cannot be changed.
Emergency Mode | Fan/EMERG | 24 | 25 | W1, W2, G | Turn on Emerg Mode | W1 turns off, AUX and G stay on | Retest when Emerg is fixed
Emergency Mode | EMERG | 24 | 30 | AUX, G | Lower setpoint to 10 | All lights go off | Retest when Emerg is fixed
Pass
11A - Forced Air Cooling + Oil Gas/Heat 1 Stage Heat, 1 Stage Cool, No Fan | [7 empty] | 4.0/Feb 11th
Heating to OFF mode | Heat/OFF | N/A | N/A | All Off | Turn the device off | Changes cannot be made to the setpoint, Any lights on will shut off.
Heating phase 1 engages once required | OFF/Heat | N/A | N/A | All Off | Turn the device on heat Raise setpoint above ambient | W1
Heating stops if ambient is raised above setpoint | Heat | 20 | 23 | W1 | Raise ambient above setpoint | All lights shut off
- Reboot | Heat | 24 | 23 | All Off | Reboot the device and wait 10 minutes | No lights come on
Heating phase 2 engages once required | Heat | 24 | 23 | All Off | Raise the setpoint to 30 | W1 comes on
Status maintained through Reboot | Heat | 24 | 30 | W1 | Reboot the device | Nothing on initially, after 10 minutes W1
Changing to Cool Mode from Heat Cooling phase 1 engages once required | Heat/Cool | 24 | 30 | All Off | Change to Cool mode Make sure ambient > setpoint | Y1 comes on
Cooling stops when ambient is lowered below setpoint | Cool | 24 | 23 | Y1 | Lower ambient below setpoint | All Lights shut off
- Reboot | Cool | 22 | 23 | All Off | Reboot the device and wait 10 minutes | No lights come on
Cooling phase 2 enagges once required | Cool | 22 | 23 | All Off | Lower setpoint to 16 | Y comes on
Status maintained through Reboot | Cool | 22 | 16 | Y1 | Reboot the device | Nothing on initially, after 10 minutes Y1
Cooling to OFF Mode | Cool/OFF | 22 | 16 | Y1 | Turn the device off | Changes cannot be made to the setpoint, Any lights on will shut off.
OFF to Cool mode | OFF/Cool | 22 | 16 | All Off | Turn the device back to cool | Y1
Cool to Heat mode | Cool/Heat | 22 | 16 | Y1 | Turn the device on heat | All lights shut off(heat is ambient 24, setpoint 23)
Pass
31O - Forced Air Heat Pump System 1 Stage Heat, 1 Stage Cool, No Fan, With EMERG, Reversing Valve for Cool | [7 empty] | 4.0/Feb 11th
Cooling engages when required | Cool | 18 | 22 | All off | Lower setpoint to 16 | Y1, W1 comes on
- Reboot | Cool | 18 | 16 | Y1, O/B | Reboot the device and wait 10 minutes | O/B stays on, Y1 comes on after 10
Cooling stops when ambient lowered below setpoint | Cool | 18 | 16 | Y1, O/B | Lower ambient to 14 | Y1 shuts off, O/B stays on
Cooling re-engages when setpoint is dropped below ambient | Cool | 14 | 16 | O/B | Lower setpoint to 12 | O/B stays on, after 18+ minutes Y1 comes on
Status maintained through Reboot | Cool | 14 | 12 | O/B, Y1 | Reboot the device | O/B on initially, Y1 after 10 minutes
Cooling stops when device is turned off | Cool/OFF | 14 | 12 | O/B, Y1 | Turn off the device | Y1 shuts off, O/B stays on after 12 mins | Andrew: Does this make sense? Why would O/B stay on if off?
Switch from OFF to Heat works as expected | Off/Heat | 24 | 20 | O/B | Turn the device on heat (S<A) | O/B stays on | Andrew: Does this make sense? Why would W1 stay on?
Heating engages when required | Heat | 24 | 20 | O/B | Raise the setpoint to 28 | O/B stays on, After 5 minutes O/B shuts off and Y1 comes on | Andrew: Does this make sense?
Status maintained through Reboot | Heat | 24 | 28 | Y1 | Reboot the device | Nothing on initially, after 10 minutes Y1
Heating stops when ambient raised above setpoint | Heat | 24 | 28 | Y1 | Raise the ambient to 30 | All lights go off
Switch from Heat to EMERG mode | Heat/EMERG | 30 | 28 | All off | Change the mode to Emerg(S<A) | Aux comes on
- Reboot | EMERG | 30 | 28 | AUX | Reboot the device and wait 10 minutes | Aux comes on | Retest when Emerg is fixed
Emergency Mode Setpoint > Ambient | EMERG | 30 | 28 | AUX | Raise the setpoint to Max, ambient to 25 | Aux comes on | Retest when Emerg is fixed
Switch from Emergency Mode to OFF | EMERG/OFF | 25 | 30 | AUX | Turn off the device | All lights go off | Retest when Emerg is fixed
66B - Forced Air Conditioning + Oil Gas/Heat 2 Stage Heat, 2 Stage Cool, with Fan | [7 empty] | 4.0/Feb 17th
Heat(phase1) engages when cool is added to the device. | Heat | 20 | 18 | All off | Lower ambient to < 18 | W1, G come on, after 10 minutes W2 comes on
Confirm proper behaviour when temp resets | Heat | 17 | 18 | W1, W2, G | Allow ambient to >=18 | W1, W2 turn off, after 3 minutes G turns off
- Reboot | Heat | 20 | 18 | All off | Reboot the device and wait 10 minutes | No lights come on
Heat(phase 2) engages when cool is added to the device. | Heat | 20 | 18 | All off | Lower ambient to < 12 | W1 , W2 and G come on
Status maintained through Reboot | Heat | 12 | 18 | All off | Reboot and wait 10 minutes | No lights come on, after 10 minutes W1, W2 and G come on.
Confirm proper behaviour when temp resets | Heat | 12 | 18 | W1, W2 and G | Allow ambient to >=18 | W1, W2 turn off, after 3 minutes G turns off
Heat(phase1) engages when Heat is added to the device. | Heat | 18 | 20 | W1, W2, G | Raise ambient to >20 | W1, W2 turn off, after 3 minutes G turns off
Confirm proper behaviour when temp resets | Heat | 21 | 20 | All off | Allow ambient to < 20 | W1, G comes on
Heat(phase 2) engages when Heat is added to the device. | Heat | 18 | 20 | W1, G | Raise ambient to > 26 | W2 comes on
Confirm proper behaviour when temp resets | Heat | 26 | 20 | W1, W2, G | Allow ambient to < 20 | W1, W2 turn off, after 3 minutes G turns off
Cool(phase1) engages when heat is added to the device. | Cool | 18 | 20 | All off | Raise ambient to >20 | Y1, G comes on, after 10 minutes Y2 comes on
Confirm proper behaviour when temp resets | Cool | 21 | 20 | Y1, Y2, G | Allow ambient to < 20 | Y1, Y2 turn off, after 3 minutes G turns off
- Reboot | Cool | 18 | 20 | All off | Reboot the device and wait 10 minutes | No lights come on
Cool(phase 2) engages when heat is added to the device. | Cool | 18 | 20 | All off | Raise ambient to < 26 | Y1, Y2 and G come on
Status maintained through Reboot | Cool | 18 | 20 | All off | Reboot and wait 10 minutes | No lights come on, after 10 minutes Y1, Y2 and G come on.
Confirm proper behaviour when temp resets | Cool | 26 | 20 | Y1, Y2, G | Allow ambient to < 20 | Y1, Y2 turn off, after 3 minutes G turns off
Cool(phase1) engages when Cool is added to the device. | Cool | 20 | 18 | Y1, Y2, G | Lower ambient to < 18 | Y1, Y2 turn off, after 3 minutes G turns off
Confirm proper behaviour when temp resets | Cool | 17 | 18 | All off | Allow ambient > 18 | Y1, G comes on, after 10 minutes Y2 comes on
86L - Forced Air Heat Pump System 2 Stage Heat, 2 Stage Cool, with Fan, With EMERG, Reversing Valve Heat
Cooling engages when required | Cool | 18 | 22 | All off | Lower setpoint to 16 | Y1 and G comes on
Cooling stops when ambient lowered below setpoint | Cool | 18 | 16 | Y1, G | Lower ambient to 14 | Y1 and G shut off
- Reboot | Cool | 14 | 16 | All off | Reboot the device and wait 10 minutes | No lights come on
Cooling re-engages when setpoint is dropped below ambient | Cool | 14 | 16 | All off | Lower setpoint to 9 | Y1, Y2 and G come on
Status maintained through Reboot | Cool | 14 | 9 | Y1, Y2, G | Reboot the device | Nothing on initially, after 10 minutes Y1, Y2 and G come on
Cooling stops when device is turned off | Cool/OFF | 14 | 12 | Y1, Y2, G | Turn off the device | All lights go off
Switch from Cool to Heat works as expected | OFF/Heat | 24 | 20 | All off | Turn the device on heat (S<A) | All lights stay off
Heating engages when required | Heat | 24 | 20 | All off | Raise the setpoint to 28 | After 5 minutes Y1, O/B, and G come on, after 10 minutes Y2
Status maintained through Reboot | Heat | 24 | 28 | Y1, Y2, O/B, G | Reboot the device | O/B on initially, G and Y1 after 5
Heating stops when ambient raised above setpoint | Heat | 24 | 28 | Y1, Y2, O/B, G | Raise the ambient to 30 | All lights go off except O/B | Andrew: Does this make sense?
Switch from Heat to EMERG mode | Heat/EMERG | 30 | 28 | O/B | Change the mode to Emerg(S<A) | Only O/B stays on | Retest when Emerg is fixed
- Reboot | EMERG | 30 | 28 | O/B | Reboot the device and wait 10 minutes | O/B stays on | Andrew: Does this make sense?
Emergency Mode Setpoint > Ambient | EMERG | 30 | 28 | O/B | Raise the setpoint to Max, ambient to 25 | AUX and G come on | Retest when Emerg is fixed
Switch from Emergency Mode to OFF | EMERG/OFF | 25 | 30 | O/B, AUX, G | Turn off the device | All lights go off except O/B | Andrew: Does this make sense?

## Summary of Issues
Bug # | Bug | Zen V1- Old Device | Version | Severity
B-002 | Temp calibration issues, we always seem to read higher by a couple of degrees minimally. Sharon is taking care of this | Reads lower but still too high | Mar 4th | Major
B-012 | We can set configurations that we have no data for and are not in the spreadsheets, i.e. 00O, 00A, 00B, 00C, 00D, and 00L. This creates a huge list of configs that take a long time to go through but it seems many are not valid or supported, what happens if these are accidentally selected, lets remove those we don't use. Sharon to decide if worth fixing | Same | Mar 4th | Trivial
| Things to Add/Questions to Ask: | Answered? | Notes
Q-1 | Cycles - when we turn on and off multiple times, change modes many times, etc what is affecting our delay times? | Yes
Q-2 | is CPH from off only, or does it include mode changes? any other factors that affect this? Andrew please provide more info. | Yes
Q-3 | Emergency Mode - How should this work? | Yes
Q-4 | What are reversing Valve Calls? Clarity on O/B/AUX | Yes
Q-5 | What is frozen/freeze protection temp, is this applicable? | Yes | Add Tests to Sheet
Q-6 | What is auto mode and is this being used? it's noted in the documentation but i have not seen it on the device. | Yes
Q-7 | There are a bunch of CONF codes on the device that are not mentioned in the spreadsheet. These include: 80A, 80B, 80C, 80D, 81A - 81P, 867A, 86B, 86C, 86D | No
Q-8 | 86K says it does not support Emerg in the sheet but on the device it does. | No
Q-9 | 90D says it does not support Emerg in the sheet but on the device it does. | No
Q-10 | 91D says it does not support Emerg in the sheet but on the device it does. | No
Q-11 | 96D says it does not support Emerg in the sheet but on the device it does. | No
Q-12 | Do we need to add a test for testing the multiple fan speed modes? or will this be removed with the fan changes? | Yes
| LV Fields in Adam's Terms | LV Fields: Definitions |  | Tested?
| Minimum Compressor on Minutes: when the device is off, this is the time it will take for it to initially come back on - Tested | For example, if the Minimum Compressor On Minutes is set to 5 minutes, the system will ensure that the compressor runs for at least 5 minutes after it is turned on, even if the thermostat reaches the set temperature earlier. After that, the system can turn off the compressor, but it won't allow it to cycle back on immediately after being turned off, which helps prevent excessive wear. In short, Minimum Compressor On Minutes is a time buffer designed to protect the compressor and optimize system efficiency by preventing it from constantly cycling on and off. |  | Yes
| Heat Stage 2 Delta: The maximum the setpoint can be over the ambient before stage 2 kicks in | In the context of low voltage thermostat systems, the term "Heat Stage 2 Delta" refers to the difference in temperature that triggers the second stage of heating to activate. Here's how it generally works: Heat Stage 1 is typically controlled by a single thermostat signal (like a standard heating system turning on the furnace or heat pump). Heat Stage 2 usually refers to a second stage of heating that kicks in if the temperature continues to drop and the first stage cannot keep up with the demand. This is more common in systems like heat pumps or multi-stage heating systems (for example, gas furnaces with multiple stages). The "delta" (often symbolizing a difference) means the temperature difference between the current room temperature and the thermostat setpoint, which must be reached or exceeded to trigger the second stage of heating. For example, if the thermostat is set to 70°F, the system might activate Stage 1 when the temperature drops to 68°F. Stage 2 might be triggered when the temperature falls further to 65°F or whatever the preset Stage 2 Delta is (often around a 2-3 degree difference). In short, Heat Stage 2 Delta is essentially the temperature threshold that needs to be reached (below the setpoint) before the system activates the second stage of heating. |  | No
| Cool Stage 2 Delta: The maximum the setpoint can be under the ambient before stage 2 kicks in | In the context of low voltage thermostat systems, "Cool Stage 2 Delta" works similarly to the Heat Stage 2 Delta, but for cooling systems. It refers to the temperature difference that triggers the second stage of cooling when the temperature rises above the thermostat setpoint and the first stage of cooling can't maintain the desired temperature. Here’s a breakdown of how it functions: Cool Stage 1 is typically the first stage of cooling, activated when the temperature rises above the thermostat setpoint by a certain degree. This could be a standard cooling system like a single-stage air conditioner or heat pump. Cool Stage 2 refers to the second, more powerful stage of cooling that kicks in if the temperature continues to rise and Stage 1 cannot keep up with the demand. It is often seen in multi-stage cooling systems (e.g., multi-stage air conditioners or heat pumps). The "Delta" in Cool Stage 2 Delta refers to the temperature difference between the thermostat setpoint and the room temperature, which must be exceeded to trigger the second stage of cooling. For example, if your thermostat is set to 75°F, Stage 1 cooling might activate if the room temperature rises to 77°F. Stage 2 might kick in when the temperature hits 80°F or higher, depending on the Cool Stage 2 Delta setting (often 3–5°F). In short, Cool Stage 2 Delta is the temperature threshold difference that triggers the second, more intensive stage of cooling when the first stage is insufficient to maintain the setpoint. |  | No
| Heat Stage 2 Delay Minutes: Time is takes for phase 2 heat to kick in after phase 1 is initialized. - Tested | Heat Stage 2 Delay Minutes refers to the amount of time the thermostat waits before activating Stage 2 heating in a multi-stage heating system after Stage 1 has been running. This delay is programmed to avoid the system from switching too quickly between stages, which could lead to inefficiency or damage. Here’s how it works: Stage 1 Heating: This is the initial stage of heating, typically activated when the temperature drops slightly below the thermostat setpoint. Heat Stage 2: If Stage 1 cannot bring the temperature up quickly enough or if the temperature continues to fall, the thermostat will activate Stage 2 heating—a more powerful heating stage (like a secondary furnace or higher output heating element). Heat Stage 2 Delay: This is the period of time the thermostat waits before switching to Stage 2 after Stage 1 has been running. For example, if Heat Stage 2 Delay Minutes is set to 5 minutes, the thermostat will not switch to Stage 2 heating until 5 minutes after Stage 1 has been running. This delay prevents the system from unnecessarily switching between stages too quickly, which could lead to inefficient operation and wear on the system. In short, Heat Stage 2 Delay Minutes is a setting that defines the waiting time before the second, more powerful heating stage is activated, allowing the system to run Stage 1 for a sufficient amount of time before escalating to Stage 2. This helps ensure efficient operation and protects the system from rapid cycling between stages. |  | Yes
| Cool Stage 2 Delta Delay Minutes: Time it takes for phase two of cool to kick in after phase 1 is initialized. - Tested | Cool Stage 2 Delay works similarly to Heat Stage 2 Delay but applies to the cooling system. It refers to the amount of time the thermostat waits before activating Stage 2 cooling in a multi-stage cooling system, after Stage 1 has been running. This delay is used to prevent rapid switching between cooling stages, ensuring more efficient operation and protecting the system from wear. Here's how it works: Stage 1 Cooling: The first stage of cooling is activated when the room temperature rises above the thermostat setpoint by a small amount. This stage typically involves a less powerful compressor or cooling unit. Cool Stage 2: If the room temperature continues to rise and Stage 1 cannot maintain the desired temperature, the system activates Stage 2 cooling. This is a more powerful stage that can cool more aggressively, often involving a higher capacity compressor or more intense cooling mode. Cool Stage 2 Delay: This setting defines the waiting time the thermostat will allow before switching to Stage 2 cooling after Stage 1 has been running. For example, if the Cool Stage 2 Delay is set to 5 minutes, the thermostat will wait for 5 minutes before activating Stage 2 cooling, even if Stage 1 isn't sufficient to meet the cooling demand right away. |  | Yes
| Heat Stage 1 CPH | Heat Stage 1 CPH stands for Heat Stage 1 Cycles Per Hour. It refers to the number of times per hour that the first stage of heating (Stage 1) can turn on and off (cycle) in a heating system, such as a furnace or heat pump. For example: If the Heat Stage 1 CPH is set to 3, the first stage of heating can turn on and off up to 3 times in one hour. If it's set to 6, the system can cycle on and off up to 6 times per hour. This setting is used to prevent short cycling (the system turning on and off too quickly), which can lead to inefficiency and wear on the equipment. By setting the CPH, the thermostat helps the system run smoothly, maintaining a more consistent temperature without unnecessarily frequent cycling. In short, Heat Stage 1 CPH helps control how often the first stage of heating turns on and off within an hour, allowing the system to heat your home efficiently while preventing rapid cycling. |  | No
| Heat Stage 2 Maximum CPH | Heat Stage 2 Maximum CPH refers to the maximum number of cycles per hour that the second stage of heating (Stage 2) is allowed to turn on and off. This setting controls how often the second, more powerful heating stage can operate during an hour. Example: If your thermostat is set with a Heat Stage 2 Maximum CPH of 3, it means that Stage 2 heating will not be allowed to cycle on and off more than 3 times in any given hour, regardless of how much additional heating is needed. Once the system reaches this limit, Stage 2 will not turn on again until the next hour. |  | No
| Cool Stage 1 CPH | Cool Stage 1 CPH (Cycles Per Hour) refers to the maximum number of cycles per hour that the first stage of cooling (Stage 1) can turn on and off in a cooling system, such as an air conditioner or heat pump. It determines how often the system can cycle on and off in an hour while trying to maintain the set temperature If Cool Stage 1 CPH is set to 3, it means the first stage of cooling can cycle on and off up to 3 times in one hour. If the temperature in the space reaches the thermostat setpoint and Stage 1 cooling is still running, it will continue to cycle until it reaches the maximum allowable CPH (in this case, 3). After that, the system won't cycle Stage 1 again until the next hour, even if the cooling demand remains. |  | No
| Cool Stage 2 Maximum CPH | Cool Stage 2 Max CPH refers to the maximum number of cycles per hour that the second stage of cooling (Stage 2) can be allowed to operate in a cooling system, such as a multi-stage air conditioner or heat pump. Here's how it works: Cool Stage 2 is typically the more powerful cooling stage in a multi-stage system. It activates when Stage 1 (the less powerful stage) can't keep up with the cooling demand, usually when the temperature continues to rise beyond what Stage 1 can handle efficiently. Max CPH defines the maximum number of times Stage 2 can turn on and off (cycle) in one hour. For example, if the Cool Stage 2 Max CPH is set to 2, Stage 2 cooling can cycle on and off a maximum of 2 times per hour. Once this limit is reached, the system won't allow Stage 2 to turn on again until the next hour, even if cooling is still needed. |  | No

## Release Notes
Release notes for LV 4.3.5: * reorganize app-datastore folder structure by @iain-mysa in https://github.com/empoweredhomes/mysa-firmware/pull/177 * Story/refactor app datastore component by @iain-mysa in https://github.com/empoweredhomes/mysa-firmware/pull/178 * Add convenience functions for mac by @bjbemister19 in https://github.com/empoweredhomes/mysa-firmware/pull/182 * Story/wake on proximity by @iain-mysa in https://github.com/empoweredhomes/mysa-firmware/pull/184 * update shadow list with physicalInterface by @iain-mysa in https://github.com/empoweredhomes/mysa-firmware/pull/186 * Story/add wifi factory reset by @spot1000 in https://github.com/empoweredhomes/mysa-firmware/pull/183 * Story/telemetry start time by @iain-mysa in https://github.com/empoweredhomes/mysa-firmware/pull/185 things to test: Brightness + wake on approach device sitting at rest will dim to 50% brightness, actions taken will bring the device up to full brightness and display arrow wifi reset, hold the up and down button simultaniously to start a countdown, at 0 device will reset wifi credentials. it should maintain state during the reset (ie if in heating to 26, should still be heating to 26 after reset) telemetry start time bug - no longer on boot should the first elemetry time be in the year 2000 haptic sounds on button presses. pairing sign with only show for 5 minutes then default back to conf menu, but disconnect icon should always show while device is not on wifi